## HSG274
HSG274 Checklist for Hot and Cold Water Systems
Service | Action to Take | Frequency | Responsibilty
Calorifiers | Inspect calorifier internally by removing the inspection hatch or using a | Annually, or as indicated by the rate of fouling | Council Approved Legionella Contractor
boroscope and clean by draining the vessel. The frequency of inspection
and cleaning should be subject to the findings and increased or
decreased based on conditions recorded
| Where there is no inspection hatch, purge any debris in the base of the | Annually, but may be increased as indicated by | Council Approved Legionella Contractor
| calorifier to a suitable drain. | the risk assessment or result of inspection
| Collect the initial flush from the base of hot water heaters to inspect | findings
clarity, quantity of debris, and temperature
| Check calorifier flow temperatures (thermostat settings should modulate as | Monthly | Council Approved Legionella Contractor
| close to 60 °C as practicable without going below 60 °C) |  | or Legionella Responsible Trained
| Check calorifier return temperatures (not below 50 °C, in healthcare |  | Person
premises not below 55 °C)
Hot water | For non-circulating systems: take temperatures at sentinel points (nearest | Monthly | Council Approved Legionella Contractor
services | outlet, furthest outlet and long branches to outlets) to confirm they are at |  | or Legionella Responsible Trained
| a minimum of 50 °C within one minute (55 °C in healthcare premises) |  | Person
| For circulating systems: take temperatures at return legs of principal | Monthly | Council Approved Legionella Contractor
| loops (sentinel points) to confirm they are at a minimum of 50 °C (55 °C |  | or Legionella Responsible Trained
| in healthcare premises). Temperature measurements may be taken on the |  | Person
surface of metallic pipework
| For circulating systems: take temperatures at return legs of subordinate | Quarterly (ideally on a rolling | Council Approved Legionella Contractor
| loops, temperature measurements can be taken on the surface of pipes, | monthly rota) | or Legionella Responsible Trained
| but where this is not practicable, the temperature of water from the last |  | Person
outlet on each loop may be measured and this should be greater than
50 °C within one minute of running (55 °C in healthcare premises). If the
temperature rise is slow, it should be confirmed that the outlet is on a
long leg and not that the flow and return has failed in that local area
| All HWS systems: take temperatures at a representative selection of other | Representative selection of other sentinel | Council Approved Legionella Contractor
| points (intermediate outlets of single pipe systems and tertiary loops in | outlets considered on a rotational basis to | or Legionella Responsible Trained
| circulating systems) to confirm they are at a minimum of 50 °C (55 °C in | ensure the whole system is reaching | Person
| healthcare premises) to create a temperature profile of the whole system | satisfactory temperatures for
| over a defined time period | legionella control
POU water | Check water temperatures to confirm the heater operates at | Monthly–six monthly, or | Council Approved Legionella Contractor
heaters (no | 50–60 °C (55 °C in healthcare premises) or check the installation has a | as indicated by the risk | or Legionella Responsible Trained
greater than | high turnover | assessment | Person
15 litres)
Service | Action to Take | Frequency | Responsibilty
Combination | Inspect the integral cold water header tanks as part of the cold water | Annually | Council Approved Legionella Contractor
water | storage tank inspection regime, clean and disinfect as necessary. If
heaters | evidence shows that the unit regularly overflows hot water into the
integral cold water header tank, instigate a temperature monitoring
regime to determine the frequency and take precautionary measures as
determined by the findings of this monitoring regime
| Check water temperatures at an outlet to confirm the heater operates at | Monthly | Council Approved Legionella Contractor
| 55–60 °C |  | or Legionella Responsible Trained Person
Cold water | Inspect cold water storage tanks and carry out remedial work where | Annually | Council Approved Legionella Contractor
tanks | necessary
| Check the tank water temperature remote from the ball valve and the | Annually (Summer) or as indicated by the | Council Approved Legionella Contractor
| incoming mains temperature. Record the maximum temperatures of | temperature profiling
the stored and supply water recorded by fixed maximum/minimum
thermometers where fitted
Cold water | Check temperatures at sentinel taps (typically those nearest to and | Monthly | Council Approved Legionella Contractor
services | furthest from the cold tank, but may also include other key locations on |  | or Legionella Responsible Trained
| long branches to zones or floor levels). These outlets should be below |  | Person
20 °C within two minutes of running the cold tap. To identify any local
heat gain, which might not be apparent after one minute, observe the
thermometer reading during flushing
| Take temperatures at a representative selection of other points to confirm | Representative selection of other sentinel | Council Approved Legionella Contractor
| they are below 20 °C to create a temperature profile of the whole system | outlets considered on a rotational basis to | or Legionella Responsible Trained
| over a defined time period. Peak temperatures or any temperatures that | ensure the whole system is reaching | Person
| are slow to fall should be an indicator of a localised problem | satisfactory temperatures for
legionella control
| Check thermal insulation to ensure it is intact and consider | Annually | Council Approved Legionella Contractor
weatherproofing where components are exposed to the outdoor
environment
Showers and | Dismantle, clean and descale removable parts, heads, inserts and hoses | Quarterly or as indicated by | Council Approved Legionella Contractor
spray taps | where fitted | the rate of fouling or other
risk factors, eg areas with
high risk patients
POU filters | Record the service start date and lifespan or end date and replace | According to manufacturer’s | Council Approved Legionella Contractor
| filters as recommended by the manufacturer (0.2 μm membrane POU | guidelines
filters should be used primarily as a temporary control measure while a
permanent safe engineering solution is developed, although long-term
use of such filters may be needed in some healthcare situations)
Service | Action to Take | Frequency | Responsibilty
Base | Visually check the salt levels and top up salt, if required. Undertake a | Weekly, but depends on the | Council Approved Legionella Contractor
exchange | hardness check to confirm operation of the softener | size of the vessel and the
softeners |  | rate of salt consumption
| Service and disinfect | Annually, or according to | Council Approved Legionella Contractor
manufacturer’s guidelines
Multiple use | Backwash and regenerate as specified by the manufacturer | According to manufacturer’s | Council Approved Legionella Contractor
filters |  | guidelines
Infrequently | Consideration should be given to removing infrequently used showers, | Weekly, or as indicated by | Council Approved Legionella Contractor
used outlets | taps and any associated equipment that uses water. If removed, any | the risk assessment
redundant supply pipework should be cut back as far as possible to
a common supply (eg to the recirculating pipework or the pipework
supplying a more frequently used upstream fitting) but preferably by
removing the feeding ‘T’
Infrequently used equipment within a water system (ie not used for a
period equal to or greater than seven days) should be included on the
flushing regime
Flush the outlets until the temperature at the outlet stabilises and is
comparable to supply water and purge to drain
Regularly use the outlets to minimise the risk from microbial growth in the
peripheral parts of the water system, sustain and log this procedure once
started
For high risk populations, eg healthcare and care homes, more frequent
flushing may be required as indicated by the risk assessment
TMV's | Risk assess whether the TMV fitting is required, and if not, remove | Annually or on a frequency | Council Approved Legionella Contractor
| Where needed, inspect, clean, descale and disinfect any strainers or | risk | or Council Approved Plumbing Contractor
| filters associated with TMVs | assessment, taking account
| To maintain protection against scald risk, TMVs require regular routine | of any manufacturer’s
| maintenance carried out by competent persons in accordance with the | recommendations
manufacturer’s instructions. There is further information in paragraphs
2.152– 2.168
Expansion | Where practical, flush through and purge to drain | Monthly–six monthly, | Council Approved Legionella Contractor
vessels |  | as indicated by the risk assessment | or Council Approved Plumbing Contractor